Proposal Draft: Node-Level Agentic Digital Twin for Predictive Thermal Orchestration

1. Scope of Work

This dissertation focuses on designing, implementing, and evaluating a node-level Agentic Digital Twin (ADT) for predictive thermal orchestration in GPU-dense AI servers. The work is scoped intentionally to a single compute node to ensure feasibility in a 20-week part-time M.Tech schedule, while still demonstrating capabilities that scale naturally to rack- and datacenter-level autonomy.

The scope includes:

### 1.1 Surrogate Thermal Model (Digital Twin Core)

Develop and calibrate a physics-guided surrogate thermal model capable of forecasting future temperature trajectories (30–90 seconds horizon), using:

- RC-based thermal surrogate (baseline surrogate; lumped-parameter physics)

  - T(t+1) = T(t) + (a·P(t) - b·Fan(t) - c(T(t) - T_amb)) Δt

- PINN-lite surrogate (optional higher-fidelity surrogate with physics-regularized ML residuals)

The surrogate must:

- accept workload, power, ambient temperature, and fan-speed inputs

- predict next-state temperature

- remain numerically stable for long-horizon rollouts

- support integration with RL as a dynamics model

### 1.2 Reinforcement Learning Control Policy

Implement a model-based RL agent that uses surrogate predictions to choose proactive cooling actions.

The RL controller must:

- map state → action (fan speed)

- reduce thermal throttling

- minimize cooling energy

- operate with constraints through a safety shield

### 1.3 Safety & Governance Layer

A lightweight safety module will:

- clamp unsafe actions

- enforce temperature constraints

- implement fallback logic when nearing thermal thresholds

- stabilize the controller (avoid oscillation)

This fulfills trustworthiness requirements for cyber-physical autonomy.

### 1.4 Simulation & Closed-Loop Integration

Construct a closed-loop autonomy environment simulating:

Telemetry → State → Twin predicts → RL chooses action → Safety filter → “Actuator” → Thermal response

The physical system will be simulated using the surrogate model calibrated from synthetic/proxy traces.

### 1.5 Baseline Controllers

Implement and compare against:

- Static fan curve

- Threshold-based cooling

- (Optional) Simplified Model Predictive Control (MPC) baseline

Out of Scope

- multi-rack CFD modeling

- real hardware integration

- full PINN (large PDE-based training)

- multi-agent coordination

## 2. Methodology Overview

The methodology consists of five integrated phases:

### 2.1 Thermal Surrogate Construction & Calibration

#### 2.1.1 RC Surrogate (Primary Surrogate)

- A lumped-parameter thermal model with coefficients (a, b, c) calibrated against synthetic traces.

- Captures heating from power, cooling from fan speed, and thermal inertia.

#### 2.1.2 Hybrid PINN-lite Surrogate (Secondary Surrogate)

- Extends RC model with a small neural network learning residual corrections.

- Includes physics-informed penalties to ensure stability.

#### 2.1.3 Teacher Model for Bootstrapping (Optional)

- A Random Forest (RF) regressor trained on synthetic data to estimate short-term thermal transitions.

- Used only for calibration sanity checks and surrogate comparison, not for RL.

#### 2.1.4 Data Sources

- Data for this study will be sourced primarily from a synthetic thermal dataset generated using an RC-based lumped-parameter model that simulates realistic GPU workload bursts, ambient temperature drift, cooling actuation, and resulting temperature trajectories. This synthetic dataset provides a controlled, reproducible environment for surrogate calibration, model-based RL training, and stress-scenario evaluation without relying on proprietary hardware logs.

- If available, supplementary real telemetry from a PowerEdge GPU server will be used strictly to refine and validate the surrogate model for a single GPU’s thermal path, while maintaining the project’s node-level CPS scope and its simulation-based RL methodology.

### 2.2 RL Environment & Dynamics Integration

#### 2.2.1 Gym-style Environment

Defines:

- State: [temp, workload, power, ambient, fan_speed]

- Actions: fan_speed ∈ [20%, 100%]

- Reward:

  - penalize throttle risk

  - penalize high energy usage

  - discourage oscillations

  - encourage staying within thermal headroom

#### 2.2.2 Surrogate as Dynamics Model

The surrogate model is used to simulate:

st+1=fθ(st,at)

This acts as the dynamics model for model-based RL.

#### 2.2.3 RL Algorithm

- SAC (Soft Actor Critic) recommended (stable in continuous action spaces)

- Model-based training for sample efficiency

- Curriculum learning:

  - start with steady workloads

  - gradually increase burstiness and stress patterns

- Domain randomization:

  - vary thermal coefficients

  - vary ambient temperature

  - inject sensor noise

### 2.3 Safety Layer Implementation

- Action clipping

- Rate limiting (smooth transitions)

- Thermal emergency override (fan=100% above threshold)

- Ensures DT-CPT trustworthiness alignment

### 2.4 Baseline Controller Implementation

#### 2.4.1 Static Fan Curve

Industry-standard piecewise temperature-to-fan rule.

#### 2.4.2 Threshold Controller

Fan=100% if temperature > threshold.

#### 2.4.3 MPC Baseline (Optional, Lightweight)

Uses surrogate to simulate:

min⁡a  J=w1⋅risk+w2⋅energy+w3⋅smoothness

Predictive horizon: 20–30 seconds
Action: first action from optimized sequence

### 2.5 Closed-Loop Execution

Full loop runs at 1–5 second intervals:

- ingest telemetry

- build state

- predict future temperatures

- agent decides action

- safety shield filters

- actuation applied

- surrogate simulates next temperature

### 2.6 Causality

- The surrogate thermal model (RC or PINN-lite) is constructed to respect cause-and-effect relationships inherent in GPU thermal dynamics.

- Cooling actions (fan speed) and physical drivers (power, workload, ambient temperature) have explicit causal influence on the next temperature state.

- The surrogate dynamics model ensures:

  - Fan ↑ → Temperature ↓

  - Workload ↑ → Power ↑ → Temperature ↑

  - Ambient ↑ → Cooling efficiency ↓

- Using a physics-guided surrogate ensures the digital twin produces physically consistent future trajectories, essential for stable predictive control.

- Causality prevents the RL agent from exploiting statistical artifacts, enabling reliable counterfactual predictions (“What happens if I increase cooling now?”).

### 2.7 Explainability

- The RC model provides interpretable parameters (a = heating, b = cooling effectiveness, c = thermal leakage), helping operators and researchers understand model behavior.

- PINN-lite maintains explainability by anchoring neural predictions to physics-derived residuals, preventing non-physical behavior.

- The twin’s predicted temperature trajectories provide transparent justification for RL decisions (e.g., raising fan speed before a forecasted thermal spike).

- The safety layer further contributes to explainability by enforcing clear, rule-based constraints (e.g., temperature ceilings, maximum actuation rates).

- Policy behavior is analyzed via:

  - action vs. predicted temperature curves,

  - throttle-risk trajectories, and

  - cooling-energy trade-offs.

- Together, the surrogate + RL agent produce decisions that can be visualized, interpreted, and validated, supporting the trustworthiness expected from cyber-physical digital twins.

## 3. Experiments & Evaluation Plan

The following experiments evaluate model fidelity, controller performance, safety, and robustness.

### 3.1 Surrogate Model Evaluation

#### 3.1.1 One-step prediction accuracy

- RC vs Hybrid RC+NN vs PINN-lite vs RF

- Metrics: MAE, RMSE

#### 3.1.2 Multi-step rollout stability

- Evaluate drift over 30–90 seconds

- Stability vs horizon

#### 3.1.3 Surrogate ablation study

- RC vs RC+NN residual

- RC vs PINN-lite

- RC vs RF baseline (pure ML)

### 3.2 RL Learning Evaluation

#### 3.2.1 Learning curves

- reward versus timesteps

- risk reduction versus timesteps

- energy use versus timesteps

#### 3.2.2 Policy behavior

- actions and temperatures under:

  - steady workloads

  - bursty patterns

  - high-power spikes

### 3.3 RL vs Baseline Controllers

#### 3.3.1 Static Fan Curve vs RL

- throttle events

- energy consumption

- control stability

#### 3.3.2 Threshold Controller vs RL

- responsiveness

- reaction time

- overshoot

#### 3.3.3 MPC vs RL

- predictive performance

- energy-tradeoff curve

- robustness

### 3.4 Safety & Trustworthiness Experiments

#### 3.4.1 With vs without safety shield

- constraint violations

- fallback activation frequency

#### 3.4.2 Robustness tests

- sensor noise

- workload spikes

- ambient temperature jumps

- partial actuator degradation

### 3.5 Predictive Orchestration Experiments (Core Contribution)

#### 3.5.1 Predictive throttle avoidance

Agent must act before temperature reaches danger zone.

#### 3.5.2 Time to cool

Compare RL vs baseline.

#### 3.5.3 Thermal headroom maintenance

Quantify mean, min, and variance.

### 3.6 Metrics

#### Primary Metrics

- Throttling event count / reduction

- Thermal headroom (°C)

- Time-to-cool after spike (s)

#### Secondary Metrics

- Cooling energy usage (normalized fan power)

- Action oscillation (variance of actions)

- Robustness (performance under stress scenarios)